## Slide 1: PACIFIC NORTHWEST REGIONAL STUDY ON GENERATION OPTIONS FOR RELIABILITY AND RESILIENCY
Jeff Dagle, PNNL
Sanjeev Pannala, WSU
Anjan Bose, WSU
Noel Schulz, WSU
November 29, 2022

## Slide 2
Compelling Issues & Challenges
  Regional observations building on NASEM report
  Consider State and Federal policies and goals
  Review utilities’ integrated resource plans
The Western Interconnection that has historically benefited from surplus capacity is now experiencing issues:
  Tightening supply with generation retirements
  Increasing volatility due to extreme weather conditions coinciding with resource availability
    (e.g., correlation between temperature extremes and wind unavailability, both summer and winter)
  Recent reliability concerns may be exacerbated with additional thermal plant retirements unless significant storage capacity is added
    Particular concern meeting peak conditions when there is a below average water year and a low wind day
Motivation
Source: 1) NASEM Report 2021, 2) PNW Utilities IRP

## Slide 3: Washington State Act: Clean Energy Transformation Act (CETA)
Senate Bill5116–passed by legislature in 2019
  Applies to all electric utilities in WA and sets specific milestones to reach required 100% clean electric supply
2025 – Eliminate coal-fired resources from serving WA customers (RCW 19.405.030)
2030 – Electric supply must be greenhouse gas neutral (RCW 19.405.040)
2045 – Electric supply must be 100% renewable or be generated from zero-carbon resources (RCW 19.405.050)
Additional policies relating to electric vehicles and building electrification
Source: WA Department of Commerce

## Slide 4: Findings from WA State Electric Utilities Integrated Resource Plans
Issues/Challenges Identified
Water availability and variability have drastic impacts on energy production and operations of the utilities
  Spring and summer hydro production levels are dependent on adequate snowpack
Major resource deficits include loss of coal generation and expiring hydro contracts
Wind generator integration has a transmission limit and often on-site storage is not economically viable
Limited energy storage is currently deployed to support grid
Central and Eastern Washington are being considered by many renewable developers as prime sites for additional renewable generation development
  Transmission congestion is an issue
Request for proposal (RFP) for a green generation being released by WA state power companies
Additional net zero requirements will be met through renewable credits or green power purchases
Uncertain adoption rates of electric vehicles and associated charging infrastructures are a challenge
Short-term capacity peak demands may not always be met by the energy imbalance market (EIM)
Energy equity
Source: WA State Utilities IRP and CEIP Reports

## Slide 5: Utilities Action Plan
Significant investments in renewable resources
Accelerated acquisition of energy conservation
Increased use of demand response
Integration of distributed energy resources like residential solar and battery energy storage
Long-duration energy storage
Reduced reliance on short-term market purchases in response to the changing western energy market
Inclusion of alternative fuels to operate new generating plants
Renewable credits
Source: WA State Utilities IRP and CEIP Reports

## Slide 6
Washington is winter peaking
Load slowly transitioning to summer peak as summer peaks increasing steadily
State load demand :43% residential, 31% Commercial, and 26% Industrial.
Transportation load increased from 7 MWh to 99 MWh between 2018-19, and the rise seems steady after that.
WA State Observations
Source: EIA data
Chart: Monthly load variations (MWh)
| January | February | March | April | May | June | July | August | September | October | November | December
2011 | 9014000 | 8487000 | 8713000 | 7849000 | 7343000 | 7335000 | 7146000 | 7366000 | 6957000 | 7021000 | 7643000 | 8852000
2012 | 8988000 | 8637000 | 8373000 | 7565000 | 7177000 | 7028000 | 7343000 | 7436000 | 6843000 | 7044000 | 7386000 | 8515000
2013 | 9257000 | 8523000 | 8160000 | 7690000 | 7202000 | 6675000 | 7413000 | 7312000 | 7001000 | 7208000 | 7491000 | 8950000
2014 | 9215000 | 8637000 | 8423000 | 7513000 | 7067000 | 6970000 | 7283000 | 7316000 | 6965000 | 7109000 | 7080000 | 8563000
2015 | 8776000 | 7683000 | 7919000 | 7468000 | 6677000 | 7042000 | 7447000 | 7265000 | 6910000 | 6899000 | 7376000 | 8655000
2016 | 8708000 | 7833000 | 7727000 | 6780000 | 6658000 | 6814000 | 7091000 | 7357000 | 6693000 | 6987000 | 7154000 | 9083000
2017 | 9528000 | 8205000 | 8265000 | 7147000 | 6928000 | 6874000 | 7299000 | 7381000 | 6852000 | 7052000 | 7567000 | 8849000
2018 | 8721000 | 8000200 | 8130000 | 7154000 | 6956000 | 6823000 | 7405000 | 7299000 | 6580000 | 7051000 | 7456000 | 8427000
2019 | 9016000 | 8345000 | 8532000 | 7214000 | 6871000 | 6702000 | 7156000 | 7320000 | 6638000 | 7306000 | 7339000 | 8615000
2020 | 8772000 | 8043000 | 8057000 | 7020000 | 6312000 | 6452000 | 6877000 | 6902000 | 6295000 | 6628000 | 7057000 | 8289000
MWh

## Slide 7
WA State: Wind and Coal
Source: EIA data
MWh
MWh
Chart: Coal
| January | February | March | April | May | June | July | August | September | October | November | December
2015 | 556000 | 2000 | 4000 | 3000 | 170000 | 552000 | 662000 | 607000 | 616000 | 653000 | 508000 | 720000
2016 | 375000 | 4000 | 3000 | 3000 | 2000 | 177000 | 620000 | 812000 | 789000 | 658000 | 443000 | 717000
2017 | 499000 | 317000 | 0 | 3000 | 3000 | 1000 | 486000 | 891000 | 862000 | 761000 | 814000 | 852000
2018 | 658000 | 64000 | 2000 | 3000 | 1000 | 86000 | 679000 | 826000 | 780000 | 803000 | 736000 | 745000
2019 | 683000 | 703000 | 645000 | 222000 | 2000 | 123000 | 736000 | 842000 | 761000 | 794000 | 793000 | 864000
2020 | 561000 | 337000 | 231000 | 2000 | 1000 | 1000 | 200000 | 598000 | 793000 | 743000 | 820000 | 884000
Chart: Wind
| January | February | March | April | May | June | July | August | September | October | November | December
2015 | 304000 | 492000 | 573000 | 681000 | 524000 | 567000 | 772000 | 717000 | 554000 | 578000 | 608000 | 707000
2016 | 438000 | 631000 | 819000 | 699000 | 797000 | 780000 | 735000 | 575000 | 684000 | 606000 | 606000 | 673000
2017 | 282000 | 441000 | 650000 | 806000 | 567000 | 772000 | 827000 | 611000 | 528000 | 664000 | 498000 | 279000
2018 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000 | 447000
2019 | 315000 | 385000 | 366000 | 764000 | 720000 | 884000 | 819000 | 688000 | 641000 | 519000 | 325000 | 253000
2020 | 931000 | 972000 | 915000 | 800000 | 784000 | 745000 | 725000 | 627000 | 501000 | 876000 | 775000 | 614000
Wind and Coal generation is 6-7% each of total generation in 2019
Coal 1459 MW and Wind 3083 MW nameplate capacity in 2019
Twice the capacity of wind produces the same energy subject wind availability
Wind generation varies significantly
  Seasonal and hourly variations
  Multi-day reduced output is of particular concern
Wind generation is low during extreme hot and cold conditions.
Coal backs up during the peak periods

## Slide 8
WA State: Hydro Stations
Source: EIA data
Chart: Hydro
| January | February | March | April | May | June | July | August | September | October | November | December
2015 | 8149000 | 8143000 | 7982000 | 6221000 | 6214000 | 5686000 | 5387000 | 5692000 | 4239000 | 4423000 | 5376000 | 5894000
2016 | 6341000 | 6367000 | 7815000 | 8115000 | 7921000 | 7260000 | 6076000 | 5330000 | 4129000 | 5191000 | 6321000 | 7479000
2017 | 7610000 | 6574000 | 8620000 | 8556000 | 9181000 | 9188000 | 7020000 | 5196000 | 4632000 | 4166000 | 4918000 | 6522000
2018 | 7973000 | 8231000 | 7510000 | 7717000 | 9465000 | 8617000 | 6819000 | 5403000 | 4038000 | 4302000 | 5428000 | 5382000
2019 | 5873000 | 5269000 | 5241000 | 5664000 | 8326000 | 6836000 | 5408000 | 5305000 | 3618000 | 3992000 | 5307000 | 5181000
2020 | 6345000 | 7046000 | 5435000 | 4783000 | 8647000 | 8780000 | 8135000 | 6230000 | 4492000 | 4596000 | 5828000 | 6092000
MWh
Hydro contributes more than 60% generation.
No new hydro stations in last decade
Hydro generation peaks during late spring and early summer periods based on water availability
Lowest hydro generation period in 2019 year
Hydro generation always varies from year to year based on seasonal climate and water availability
As Hydro availability decreases over the summer, natural gas is used to make up the deficiency

## Slide 9
Produces more than 12% of total generation
Natural gas capacity was available to produce 15,729 thousand MWh in 2019 compared to 4,848 thousand MWh in 2011.
No significant additions have been made since 2011
Increased use of gas generation over the past 3 years
Usage of gas plants tends to continue until alternate renewable options are to be identified to replace the coal plants.
WA State: Natural Gas
Source: EIA data
Chart: Natural Gas
| January | February | March | April | May | June | July | August | September | October | November | December
2015 | 618000 | 226000 | 591000 | 586000 | 781000 | 1367000 | 1687000 | 1483000 | 1476000 | 1530000 | 1435000 | 1266000
2016 | 1317000 | 955000 | 494000 | 278000 | 584000 | 775000 | 1289000 | 1649000 | 1430000 | 626000 | 583000 | 1002000
2017 | 1258000 | 579000 | 239000 | 277000 | 265000 | 223000 | 1288000 | 1679000 | 1266000 | 1364000 | 1016000 | 1395000
2018 | 676000 | 525000 | 818000 | 440000 | 310000 | 629000 | 1735000 | 1864000 | 1722000 | 827000 | 165000 | 825000
2019 | 1550000 | 685000 | 957000 | 757000 | 339000 | 1022000 | 1948000 | 2082000 | 1889000 | 1358000 | 1264000 | 1878000
2020 | 1428000 | 1042000 | 1723000 | 1542000 | 323000 | 276000 | 914000 | 1425000 | 1787000 | 1386000 | 768000 | 1402000
MWh

## Slide 10: WA State Generation-Load Scenario
Fuel Source | Generators | Facilities | Nameplate Capacity (Megawatts) 2019 | Percentage by Capacity | Generation (MWh) 2019 | Percentages of Energy
Coal | 2 | 1 | 1,459.8 | 4.6% | 7,168,000 | 6.73%
Hydroelectric | 287 | 76 | 21,177.1 | 66.6% | 66,020,000 | 62.06%
Natural Gas | 44 | 18 | 4,116.4 | 12.94% | 15,729,000 | 14.78%
Nuclear | 1 | 1 | 1,200.0 | 3.77% | 8,866,000 | 8.33%
Wind | 24 | 21 | 3,083.4 | 9.69% | 6,679,000 | 6.27%
Biomass | 49 | 16 | 402.1 | 1.26% | 1,543,000 | 1.45%
Solar, thermal and Photovoltaic | 2 | 2 | 19.7 | 0.061% | 43,000 | 0.04%
Others (Petroleum) | 18 | 8 | 335.9 | 1.05% | 321,000 | 0.3%
All Sources | 427 | 137 | 31,794.4 | 100% | 106,369,000 | 100%
Source: EIA
Winter and Summer peak demand in 2019 are 18,258 MW and 14,489 MW
Winter and Summer peak demand in 2020 are 17,254 MW and 14,843 MW

## Slide 11
Wind based power generation has greater potential in comparison to solar generation
Wind is contributing highest among all the other renewable energy sources 6% generation
Variations of wind plant productions analyzed (utilizing EIA data)
  Wind capacity factors represent wind generation availability and generation pattern for a month
  Wind capacity factors widely vary from two utilities in the same state that reflects geographical location play major roles
  There is no single variability profile showcasing complete WA state level generation and average indices still are not effective for planning wind resources
  In the same year, capacity factors for January month from two different utilities profile drastically vary from 0.2 to 0.4
  There is no single wind plant average capacity that meets all the year-long wind intermittency
  Coal generation supports winter peak load heavily and needs high wind plant capacity to match the same level of coal generation
WA State Coal Generation Replacement Study
Source: 1) EIA data, 2) Utilities IRP, 3) WA Department of Commerce
Goal: Wind and energy storage are considered as alternate resources to replace the 6.7% coal generation in WA state data

## Slide 12: Assumptions for WA State Case Study
A list of assumptions made in this particular case study are
BESS MW capacity will be the same as Coal Plant Capacity.
Generation and load data from Energy Information Administration (EIA) sources capture state-level level data precisely.
EIA platform considers state boundaries to fetch and compile all the electricity data
Maximum hourly generation from the Wind and Coal plant represent its plant MW capacity in that month of the year.
Wind plant assumed to have zero losses from power electronic conversion stages.
All the battery energy storage system (BESS) technology has 80% roundtrip efficiency
Utility-1 and Utility-2 wind profile restate state level wind profile
Normalized profile from Utility-1 and Utility-2 hourly wind data considered to extrapolate the WA state level generation in each month

## Slide 13
For Jan and Dec month, the wind capacity factor differs by 0.2.
There is no direct correlation between one plant to another.
All the wind pants in the same location lead to congestion and management problems.
Geographical diversification provides a more flexible generation
Wind Variability
Source: EIA data
Capacity factor
Chart: Wind Capacity Factors
| January | February | March | April | May | June | July | August | September | October | November | December
Utility-1 Wind | 0.40728 | 0.40114 | 0.2686 | 0.4274 | 0.34608 | 0.35632 | 0.24303 | 0.21404 | 0.32851 | 0.37517 | 0.29093 | 0.35187
Utility-2 Wind | 0.2294 | 0.23464 | 0.20168 | 0.41195 | 0.31172 | 0.40595 | 0.31719 | 0.29072 | 0.3272 | 0.28174 | 0.26556 | 0.14884

## Slide 14
For the same coal generation in Jan.2019 month, Wind nameplate capacity doubled w.r.to 0.2 and 0.4 capacity factors.
Accurate wind variability factors are required to estimate actual wind
For 6.7% coal generation replacement, more than double the existing nameplate capacity is needed (i.e. 7802MW)
This does not even guarantee steady hourly generation like a coal plant.
Storage system is must to make it a dispatchable source.
Required Wind Nameplate Capacities
Source: EIA data
MW
Chart: Wind Nameplate Capacity required
| January | February | March | April | May | June | July | August | September | October | November | December
Utility-1 Wind | 2253.981 | 2355.5439 | 3227.6636 | 698.1431 | 7.7674 | 463.9668 | 4070.4467 | 5287.4535 | 3113.6408 | 2844.6037 | 3663.604 | 3300.3746
Utility-2 Wind | 4001.7714 | 4027.0291 | 4298.6199 | 724.3217 | 8.6237 | 407.2507 | 3118.8005 | 3892.8443 | 3126.0801 | 3787.9098 | 4013.6996 | 7802.067

## Slide 15: Comparison of Generation- Jan 2019 & 2020
Chart: 2019 Generation Scenario in MW-Hourly

Fig. Generation profile-Jan. 2019

## Slide 16: Comparison of Generation- Jan 2019 & 2020
Chart: 2020Generation Scenario in MW-Hourly

Fig. Generation profile-Jan. 2020

## Slide 17: Wind Variability Observations
Average monthly capacity factor of wind generation in WA state is 0.33 and lowest is 0.20
Wind annual capacity factor considered in most of the IRP reports is 0.35
Monthly Wind capacity factor drops below 0.33 in March, July, Aug, and Nov.
Battery energy storage system roundtrip efficiency assumed to be 80%
Daily average zero wind hours are 4 hrs per day
Total below-average wind generation hours are 14 hrs per day
In the worst month, continuous zero wind hours are 59 hrs ≈ 2.5days
If we count very low generation hours, then continuous non-available wind days are ≈3 days

## Slide 18
For same January month, two wind capacity-based generators give different battery energy storage capacities
  As the wind plant capacity factor increases, the needed battery energy storage capacity decreases
In our test month (January 2019), to provide equivalent dispatched energy to the statewide coal generation:
  One example, with 4002 MW wind capacity and 0.23 capacity factor, required 360,000 MWh battery energy storage capacity
  For another example, 7802 MW wind capacity with respect to the worst capacity factor of the year, required 110,000 MWh battery energy storage capacity
Caveats: This test month does not apply to any other months. Also, the operational dispatch strategy for the storage would likely be significantly different than shown here for illustrative purposes.
Replacement Study for January Month
Source: 1) EIA data, 2) Utilities IRP, 3) WA Department of Commerce

## Slide 19
Replacement Study for January Month
Source: 1) EIA data, 2) Utilities IRP, 3) WA Department of Commerce
Chart: Generation Scenario in MW-Hourly

Chart: With Wind-4002MW

Chart: With Wind-7802 MW

## Slide 20: Wind + BESS Variation Study- Jan, May, Dec. 2019
Chart: Jan. Wind-7802 MW
Chart: May with 7802 MW
Chart: Dec. with Wind-7802 MW
Last label indicates one week interval with fixed SoC at the end of cycle.
100% discharge

## Slide 21: Observations
One week interval is considered as cycle for BESS with 100%
There is no concrete source to recharge huge BESS at the end of week or day to 100% for next day until full wind generation available.
2.5-5 days of back up energy needed with Base load equivalent value for each week (here considering Max wind Plant capacity from all the months)
Example :1460*2.5*24=87600 MWh for a given month
In each month, few continuous days are zero wind hours Same week decides BESS sizing overall.
Remaining weeks still maintain close to the same 60-80% end of the week
No direct coincidence of continuous zero wind days from one to another year
BESS and Wind Plant capacity are sensitive to Weather

## Slide 22
Weekly BESS charge/discharge cycles considered.
One-week interval is considered as a cycle for BESS with 100% SoC
2.5-5 days of backup energy needed with Base load equivalent value for each week.
Minimum BESS MWh is needed matches with weekly BESS capacity since continuous non-available wind hours match with weekly interval
If there is a reliable source to compensate continuous non-wind available periods, then Significant amount of BESS capacity reductions can occur.
Weekly BESS Cutoff simulations for Jan. 2019
Source: 1) EIA data, 2) Utilities IRP, 3) WA Department of Commerce
Chart: With Wind-7802 MW
Chart: With Wind-7802 MW
Without BESS weekly cutoff SoC
With weekly cutoff SoC

## Slide 23: Summary
Coal generation of 7% replacement demands a 300% increase in wind deployment+ 250,000MWh storage to ride through a worst month in 2019
Wind plant capacity factors vary drastically based on weather
  Planning for storage capacity should consider benchmark worst-case scenarios
  In each month, a continuous days with low or no wind generation hours determine equivalent battery energy storage requirements to provide equivalency to dispatchable generation
While replacing coal with wind + storage appears viable, there is an immense storage capacity required to achieve equality between the dispatchability of resources
It's optimal to have large wind farms with higher capacities to minimize storage capacity during normal conditions. During extreme weather scenarios, alternate supplies must be considered to avoid oversized storage.
Future work will consider additional benefits associated with cost-effective long-duration energy storage and end-use demand flexibility.